
Optimal Output Control:  Load Frequency Control of a Large Power System

Mariano,  S.J.P.S.a,   Pombo,  J.A.N.a,   Calado  M.R.A.a,   Ferreira,  L.A.F.M.b
aDepartment of Electromechanical Engineering, University of Beira Interior, 
C. Fonte do Lameiro, 6201-001 Covilhã, Portugal

bDepartment of Electrical Engineering and Computers, Instituto Superior Técnico, 
Technical University of Lisbon, Av. Rovisco Pais, 1049-001 Lisbon, Portugal

sm@ubi.pt,  m2211@ubi.pt,  rc@ubi.pt,  lmf@ist.utl.pt
Abstract—This paper addresses the stabilization and performance of the load frequency regulator.  The problem is solved by using the theory of the optimal control. An algorithm, based on the new technique, proposed by the authors, to overcome the difficulties of specifying the weighting matrices Q and R, is presented.  The algorithm here proposed considers the multi-area electric energy system. The paper presents illustrative numerical simulation results for this model.  The results indicate that the obtained controller exhibits better performance then those based on classic control.

Keywords—Generation of electrical energy, Optimal control, Control methods for electrical systems.

I. Introduction
The objective of the automatic generation control (AGC) of a power system is to maintain the frequency of each area and tie-line power flow (in interconnected system) within specified tolerance. Many investigations in the area of AGC problem of interconnected systems have been reported in the past. A number of control schemes have been employed in the design of load frequency controllers in order to achieve better dynamic performance.

The application of the optimal control theory to power systems has shown that an optimal load frequency controller can improve the dynamic stability of a power system [1], some difficulties to apply this technique still remain, mainly because (1) the optimal control is a function of all the states of the system, in practice all the states may not be available, the inaccessible states or missing states are required to be estimate, (2) it may not be economical to transfer all the information over long distances and (3) the specification of matrices Q and R [2].

The problem of selecting the weighting matrices Q and R has shown up in optimal control design [1,3]. Assigning appropriate values to the matrices Q and R in a systematic manner, together with the determination of the optimal output controller, is a major concern and is the main point addressed in this paper.

This paper develops a new practicable decentralized structures control algorithm that is based upon the authors previous results [4].  This new approach only requires the information available of the systems states in each area.

II. Background
To design a linear optimal control, a linearized model of the power system is sought. The linear model of the system is described in state space form, as



[image: image1.wmf]x

C

y

u

B

x

A

x

=

+

=

&

   
[image: image2.wmf]y

u

x

n

n

n

y

u

x

Â

Î

Â

Î

Â

Î

,

,

.
(1)

where A and B are system matrices, x the state vector, u the control signal vector, y the output vector and nx, nu and ny are the number of state, control and output variables, respectively.

Consider first that the complete state x is available for feedback. Then it is possible to allocate the set of closed-
-loop system poles to an arbitrary position by means of a suitable linear state feedback. Thus the control law is



[image: image3.wmf]x

K

u

-

=

,
(2)

where k is the feedback gain matrix.

When the number of output variables ny is less than the order of the system nx, then it is always possible to allocate ny poles of the closed-loop system. Unfortunately, we can not assign the location of the remaining (nx–ny) poles of the closed-loop system [3].

As the location may be arbitrary, the first step in pole assignment is to decide on their location. To choose the location of the poles, one should bear in mind that the required physical effort is dependent on the distance to the imaginary axis. Particularly, zeros in open loop attract poles, being very difficult to remove the poles near zeros. Consequently, for an arbitrary location, the control vector could lead to physically or economically undesired action. These considerations lead to the linear optimal regulator problem.
For the linear system described in (1), the optimal control signal u that minimizes the performance index



[image: image4.wmf]0

TT

JxQxuRu dt

¥

éù

=+

ëû

ò


(3)

is a linear function in terms of the system state variables x as [1,5]



[image: image5.wmf]x

P

B

R

x

K

u

T

1

-

-

=

-

=

,
(4)

where Q and R are the weighting matrices and P is the solution of the matrix Riccati equation



[image: image6.wmf]0

1

=

+

-

+

-

Q

P

B

PBR

PA

P

A

T

T

.
(5)

Riccati equation is the key to obtain the optimal control. Once the matrices Q and R are known, the matrix P can be obtained by solving the Riccati equation. From equation (4) one gets the optimal control vector u.

So far it was assumed that the complete state x is available for feedback. That assumption is unrealistic for the most of the systems. Usually, only a reduced number of state variables, or a linear combination thereof, are available — the so-called output vector y. In that case, it is necessary to recur to output feedback.

Therefore, suppose that the control vector must be directly obtained from the system output [6]:



[image: image7.wmf]y

F

u

-

=

,
(6)

where F is the feedback gain matrix. The linear model of system (1) can be rewritten as



[image: image8.wmf][

]

x

BFC

A

x

-

=

&

.
(7)

Let 
[image: image9.wmf][

]

BFC

A

A

-

=

D

*

. The F matrix, for which the control vector u is optimal, minimizes the performance index (3):



[image: image10.wmf][

]

1

*

*

*

1

-

-

=

C

CL

C

L

K

B

R

F

T

T

.
(8)

The matrix 
[image: image11.wmf]K

*

 is a positive semi-definite solution of 



[image: image12.wmf]0

*

*

*

*

=

+

+

+

RFC

F

C

Q

K

A

A

K

T

T

T


(9)

and 
[image: image13.wmf]L

*

 is a positive definite solution of



[image: image14.wmf]0

*

*

*

*

=

+

+

I

L

A

A

L

T

.
(10)

In the special case that 
[image: image15.wmf]C

-

1

 exists, the result is identical to that obtained with the optimal state feedback, and (8) reduces to



[image: image16.wmf]1

*

T

1

-

-

=

C

K

B

R

F


(11)

and (9) becomes



[image: image17.wmf]0

*

T

1

*

*

T

*

=

-

+

+

-

K

B

BR

K

Q

K

A

A

K

.
(12)

To obtain the optimal gain matrix F, it will be necessary to apply an iterative method. The following computer algorithm can be used [6].

Let



[image: image18.wmf][

]

1

T

1

T

1

1

T

1

1

-

-

-

-

-

-

=

C

CL

C

L

K

B

R

F

n

n

n

n

,
(13)

where 
[image: image19.wmf]K

n

 is solution of



[image: image20.wmf][

]

[

]

0

1

T

1

T

T

1

1

=

+

+

+

-

+

-

-

-

-

-

C

RF

F

C

Q

K

C

BF

A

C

BF

A

K

n

n

n

n

n

n


(14)

and 
[image: image21.wmf]1

-

n

L

 is solution of



[image: image22.wmf][

]

[

]

0

1

1

T

1

1

=

+

-

+

-

-

-

-

-

I

L

C

BF

A

C

BF

A

L

n

n

n

n

.
(15)

Start by guessing the initial value for 
[image: image23.wmf]F

0

. Then, by (14) and with 
[image: image24.wmf]n

=

1

, obtain 
[image: image25.wmf]K

1

. Substitute 
[image: image26.wmf]K

1

 into (13). 
[image: image27.wmf]F

1

 is still unknown, but it depends only on 
[image: image28.wmf]L

1

. Substituting 
[image: image29.wmf]F

1

 into (15) one gets a nonlinear equation in only one unknown, 
[image: image30.wmf]L

1

. Equation (15) is then solved for a positive definite 
[image: image31.wmf]L

1

. This value of 
[image: image32.wmf]L

1

 is substituted into (13) to give 
[image: image33.wmf]F

1

. This completes the first iteration. The value of 
[image: image34.wmf]F

1

 initiates the next iteration [6].

The foregoing has been a brief review of optimal control theory as it applies to the optimal load frequency regulator problem. However, in order to design the  load frequency regulator, a major problem still remains: how to select the matrices Q and R.  Next we present a technique for specifying the matrices Q and R in the context of optimal state feedback.

III. Proposed Approach
In this paper, without loss of generality, the weighting matrix R is specified as an identity matrix. Thus, the problem then is to specify the weighting matrix Q.
The most common procedure to specify the matrix Q is search by trial and error. Different matrices 
[image: image35.wmf]i

Q

 result in different gain matrices 
[image: image36.wmf]i

F

, which in turn result in different dynamic performances for the closed-loop system. There are many possibilities to test by trial and error, which makes this procedure burdensome.
In order to simplify and accelerate this procedure of trial end error, or even avoid it altogether, a new algorithm, based on [4], to select the weighting matrix Q is proposed.
When the location of the systems poles is assigned, and a suitable gain matrix F is computed, then it is possible to judge on the weight of each state variable upon the control vector.  An initial weighting matrix 
[image: image37.wmf]0

Q

 may then be selected.  This matrix plays a decisive role in making the system poles move close to the desired pole locations, as done by conventional pole assignment techniques.

Algorithm
Step 1-
Specify desired location for system poles.
Step 2-
Compute the corresponding gain matrix F to 
allocate the poles 
[image: image38.wmf]L

 in the desired location.
Step 3-
Let 
[image: image39.wmf](

)

F

diag

Q

=

0

 (i.e.  Initialize 
[image: image40.wmf]Q

).


Step 4-
Vary each value of 
[image: image41.wmf]Q

0

, one by one, and compute 
the eigenvalues of the closed-loop system:


for
i=1 : n



[image: image42.wmf]0

Q

Q

i

=



for
j=1 : 
[image: image43.wmf](

)

0

max

,

max

Q

of

value

i

i

Q

for

value

i




[image: image44.wmf]j

i

i

Q

i

i

Q

i

i

´

=

)

,

(

)

,

(



compute 
[image: image45.wmf] 

ij

L




end

end
Step 5-
Retrieve Q for the desired pole location.

Notes:

The more negative the real parts of the eigenvalues specified in step 1 are, the larger the elements values of 
[image: image46.wmf]0

Q

 will be.
Step 4 imposes a maximum value for the elements of the weighting matrix Q, as expressed by 
[image: image47.wmf](

)

i

i

Q

for

value

i

,

max

. This prevents feedback gains from becoming too large.
As an example, the value of 
[image: image48.wmf]i

Q

 is computed ten times with an increment in j of five, for max value for 
[image: image49.wmf](

)

100

,

=

i

i

Q

i

.
To select the value for 
[image: image50.wmf])

,

(

i

i

Q

i

 (step 5), it is convenient to draw the locus of the eigenvalues.

IV. Test Results
For an interconnected system with a large number of generating units, modeling the power control system of each individual generator is complex.  Although, simpler models of lower dimension give more understandable results.  In general, we may identify groups of generators which are closely coupled internally but relatively weakly coupled between groups.  The model and its usefulness are enhanced when the boundaries of the coherent groups of generators coincide with those of an operating company or utility.  In this case, under a single operating jurisdiction, the generators are frequently controlled as single unit and in such case the groups are called control areas.
To illustrate the proposed algorithm a four different interconnected areas are considered: one area with hydro power plants(area 1, two with fossil power plants, one with nonreheat steam system configuration(area 2 and the other one with tandem compound, single reheat steam system configuration(area 3 and the last area is considered to have infinite kinetic energy(area 4, as shown in Fig. 1.

This case study can be compared to an interconnection of the power systems of individual utilities.  Each company operates independently within its own jurisdiction, but there are contractual agreements about intercompany exchanges of power through the tie-lines and other agreements about operating procedures to maintain system frequency.  The adjustment of the command increment, 
[image: image51.wmf]i

r

P

D

, is done automatically and according to the contractual agreements.

We have combined the referred four-area system and the model was obtained. This model is shown in Fig. 2, using a block diagram representation, and the system is defined by the symbols and parameters shown in Appendix, where 
[image: image52.wmf]i

p

D

K

1

=

 and 
[image: image53.wmf]i

i

p

D

H

T

2

=

.

[image: image54.wmf]
Fig.1 – Case study ( four interconnected control areas

As a result a linear model of the system, in state space form, is obtained:



[image: image55.wmf]D

xAxBuP

=++GD

&

.
(16)

The state vector is defined as


[image: image56.wmf]123

123123

123int,1int,2int,3

12

[

]

MMxxM

EEECCC

xfffppp

ppppp

xxxppp

=DDDDDD

DDDDD

DDDDDD

MM

M

M

.

The control vector and incremental load demand change vector are defined, respectively, as


[image: image57.wmf]1

2

3

r

r

r

p

up

p

D

éù

êú

=D

êú

êú

D

ëû

, 
[image: image58.wmf]1

2

3

D

DD

D

p

Pp

p

éù

D

êú

D=D

êú

êú

D

êú

ëû

.

Substituting the definition of the states and the control into to the seventeen differential equations that define the four-area system we can obtain, respectively, the control matrix B, the disturbance matrix 
[image: image59.wmf]G

 and the state matrix A, that it results in a controllable system but not observable.

[image: image60.wmf]11

2

3

'

11

000000000000000

0.5

1

0000000000000000

1

0000000000000000

GG

G

G

TT

B

T

T

éù

-

êú

êú

êú

êú

=

êú

êú

êú

êú

ëû

,


[image: image61.wmf]1

1

2

2

3

3

'

0000000000000000

0000000000000000

0000000000000000

P

P

P

P

P

P

K

T

K

T

K

T

éù

-

êú

êú

êú

-

êú

G=

êú

êú

-

êú

êú

ëû

,


[image: image62.wmf]11

111

22

222

33

333

121311213

212123223

313231323

1

00000000000000

1

00000000000000

1

00000000000000

00000000000000

00000000000000

00000000000000

1

0.

PP

PPP

PP

PPP

PP

PPP

i

i

i

KK

TTT

KK

TTT

KK

TTT

TTTTT

TTTTT

TTTTT

A

-

-

-

-

-

-

++--

-++-

--++

=

1

111

111

1

11

22

3

112221

31233231

1

2

11

0000000000000

50.50.50.5

11

000000000000000

11

000000000000000

11

000000000000000

1

0000000000000

111

00000000000000

1

0

GW

GWGWG

tt

GGG

G

TT

RTTTTT

TT

TT

TT

K

KKKKKK

TTTTTTTT

RTTT

RT

+

--

-

-

-

-

--+-

--

-

222

333

1

2

3

3

11

0000000000000

111

00000000000000

0000000000000000

0000000000000000

0000000000000000

GG

GGG

i

i

i

TT

RTTT

K

K

K

éù

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

êú

-

êú

êú

êú

--

êú

êú

êú

ê

-

ê

-

ê

ê

-

ê

ëû

ú

ú

ú

ú

ú

.
[image: image63.wmf]
Fig.2 – Block diagram of four-area perturbation model.
Applying the proposed algorithm, for the parameters given in appendix, we can specify the weighting matrix Q,


[image: image64.wmf]])

8

8

8

5

.

8

5

.

8

5

.

8

68

68

68

68

68

8

8

8

85

85

85

([

M

M

M

M

diag

Q

=

,

corresponding to state variables.

The output feedback gains matrix, F, respectively, for the state variable according to the control area i, is defined as:


[image: image65.wmf][

]

SPINTTRCI

FFFFFF

=

MMMM

.

This gain matrix F, for convenience and with purposes of more understandable presentation of results, is subdivide into five submatrixes corresponding, respectively, to the output feedback gains of the state variable according to the control area i (
[image: image66.wmf]SP

F

 ( feedback gains for the incremental frequency deviation, 
[image: image67.wmf]INT

F

 ( feedback gains for the net incremental real power exported from area i, 
[image: image68.wmf]T

F

 ( feedback gains for the governor, 
[image: image69.wmf]CI

F

 ( feedback gains for the integral control) and are:


[image: image70.wmf]7.7300

010.750

0010.04

SP

F

éù

êú

=

êú

êú

ëû

,    
[image: image71.wmf]15.0400

02.410

003.21

INT

F

-

éù

êú

=-

êú

êú

-

ëû

,


[image: image72.wmf]3.070000

013.12000

005.2910.382.40

T

F

éù

êú

=

êú

êú

ëû

,


[image: image73.wmf]22.3300

02.690

003.45

R

F

éù

êú

=

êú

êú

ëû

,    
[image: image74.wmf]1.8300

02.460

001.88

CI

F

-

éù

êú

=-

êú

êú

-

ëû

.
The corresponding eigenvalues for the system without and with optimal output control are shown in Table I.

TABLE I. 
System Eigenvalues For Both Conventional And 
Optimal Output Control

	System eigenvalues with conventional control
	System eigenvalues with optimal output control applied

	-24.75
	-212.00

	-10.80
	-16.31

	-5.28
	-4.29

	-6.19
	-2.50

	-3.30
	-0.28

	-2.72
	-17.79 ( j8.68

	-1.68
	-12.96 ( j6.35

	-0.35 ( j4.25
	-2.61 ( j1.95

	-0.25 ( j3.22
	-0.84 ( j2.32

	-0.30 ( j1.56
	-0.5 ( j0.06

	-0.87 ( j1.34
	-0.23( j 0.09

	-0.20 ( j0.38
	


A 10% step-load increase (
[image: image75.wmf]pu

P

D

1

.

0

=

D

MW) is applied to area 1 and subsequent deviations of 
[image: image76.wmf]1

f

D

, 
[image: image77.wmf]2

f

D

, 
[image: image78.wmf]3

f

D

 and 
[image: image79.wmf]1

int,

P

D

, 
[image: image80.wmf]2

int,

P

D

, 
[image: image81.wmf]3

int,

P

D

, 
[image: image82.wmf]¥

D

int,

P

 are studied. Fig. 3 and Fig. 4 illustrate the time evolution of the system frequency deviations, for each area, with classic control and with optimal output control, respectively. Fig. 5 and Fig. 6 illustrate the time evolution of the tie-line power deviation, for each area, with classic control and with optimal output control, respectively.

From these results, along with many others obtained but not discussed herein, some conclusions can be made: (1) the performance of the system with decentralized optimal output state feedback controller, Fig. 4 and Fig. 6, exhibits better damping than with the conventional control (Fig. 3 and Fig. 5) ( optimal output controllers are especially effective in damping fast the oscillatory tie-line load and frequency deviations; (2) considering the system eignevalues, was expected the increase of the stability margin of optimal solution as Fig. 4 and Fig. 6 shows.

[image: image83.wmf]
Fig.3 – Step response of system frequency deviations with classic control

[image: image84.wmf]
Fig.4 – Step response of system frequency deviations with optimal output state feedback controller
The longer term effects, as shown in Fig. 3 and Fig. 4, shows that, since the outside world is infinite (one area considered to have infinite kinetic energy), frequency is essentially back to normal and therefore the powers of each area are back to normal, by increasing the mechanical power on area 1 ( the basic principle of pool operation (scheduled interchanges of tie-line power are maintained and each area absorbs its own load changes) are satisfied. Thus, the interconnection is effective on delivering power to the control area 1, specially with optimal control where the step-load increase in area 1 is satisfied simultaneous and in equal parts, in the first second, by the other areas and, in the next seconds, by the area considered to have infinite kinetic energy.

Also, by examining the optimal gains, it is seen that the gains, corresponding to the incremental frequency deviation variable and to the net incremental real power exported from area i, impose more influence by this states, with less significant contribution of the other states.

[image: image85.wmf]
Fig.5 – Step response of system tie-line power deviation with classic control
[image: image86.wmf]
Fig.6 – Step response of system tie-line power deviation with optimal output state feedback controller

V. Conclusion
The frequency control problem of a large power system (a multi-area electric energy system) was solved through the application of a new technique that allows the specification of the weighting matrices Q and R.  As a conclusion, the optimal output state feedback, together with the proposed algorithm for specifying Q and R, yields results that are robust, and according to the desired performance.

References

[1] Charles E. Fosha e Olle I. Elgerd, The Megawatt-Frequency Control Problem: A New Approach Via Optimal Control Theory, IEEE Trans. on PAS, Vol. PAS-89, No. 4, Abril 1970.

[2] Mathur H.D. and Ghosh S. A Comprehensive Analysis of Intelligent controllers for load frequency control. In the Proceedings of IEEE Power India 2006 Conference. Delhi. April 10-12, 2006.

[3] Milan Calovic, Linear Regulator Design for a Load and Frequency Control, IEEE Trans. on PAS, Vol. PAS-91, pp.2271-2285, 1972. 

[4] S.J.P.S. Mariano, L.A.F.M. Ferreira, A Procedure to Specify Q and R for an Optimal Voltage Regulator, Proceedings of the IASTED International Conference, Las Vegas, USA, 1999

[5] L. A. F. M. Ferreira, Teaching Power Systems Control and Operation Using General-Purpose Software Technologies, 11th Power Systems Computation Conference, PSCC-93, Avignon, France, Sep 1993.

[6] William S. Levine, Michael Athans, "On the Determination of the Optimal Constant Output Feedback Gains for Linear Multivariable Systems", IEEE Trans. on Automatic Control, vol. AC-15, Nº 1, February 1970.

[7] Working Group on Prime Mover and Energy Supply, Dynamic Models for Fossil Fueled Steam Units in Power System Studies, IEEE Trans. on Power Systems, Vol. 6, No. 2, Maio 1991.

[8] A report of the AGC Task Force of the IEEE/PES/PSE/System Control Subcommitte, Understanding Automatic Generation Control, Trans. on Power Systems, Vol. 7, No. 3, Agosto 1992.
[9] J.A. Rovnak, R. Corlis, Dynamic Matrix Based Control of Fossil Power Plants, IEEE Trans. on Energy Conversion, Vol. 6, No. 2, June 1991.

Appendix

System symbols and parameters


[image: image87.wmf]i

f

D


incremental frequency deviation in area i

[image: image88.wmf]i

M

P

D


incremental generated real power (mechanical power) 
deviation in area i

[image: image89.wmf]1

x

P

D

 and 
[image: image90.wmf]2

x

P

D

 incremental  fraction generated power in 
tandem compound, single reheat turbine

[image: image91.wmf]i

D

P

D


incremental load demand change in area i

[image: image92.wmf]i

r

P

D


incremental command signal to governor speed changer in 
area i

[image: image93.wmf]i

P

int,

D

net incremental real power exported from area i

[image: image94.wmf]¥

D

int,

P

 net incremental real power exported from area 
considered to have infinite kinetic energy

[image: image95.wmf]i

H


inertia constant (
[image: image96.wmf]06

.

0

1

=

H

, 
[image: image97.wmf]1

.

0

2

=

H

 and 
[image: image98.wmf]16

.

0

3

=

H

 
in seconds)

[image: image99.wmf]i

G

T


governor time constant (
[image: image100.wmf]08

.

0

1

=

G

T

, 
[image: image101.wmf]1

.

0

2

=

G

T

 and 

[image: image102.wmf]2

.

0

3

=

G

T

 in seconds)

[image: image103.wmf]i

R


drop constant (
[image: image104.wmf]5

1

=

R

, 
[image: image105.wmf]5

.

2

2

=

R

 and 
[image: image106.wmf]6

.

2

3

=

R

 in 

[image: image107.wmf]MW

pu

Hz

)


[image: image108.wmf]ij

T


transmission constant (considered equal for all 
interconnections, 
[image: image109.wmf]5

.

0

=

ij

T

 in 
[image: image110.wmf]Hz

MW

pu

)


[image: image111.wmf]w

T


hydro turbine time constant (
[image: image112.wmf]1

.

0

=

w

T

 in seconds)

[image: image113.wmf]T

T


nonreheat turbine time constant (
[image: image114.wmf]3

.

0

=

T

T

 in seconds)

[image: image115.wmf]1

T

, 
[image: image116.wmf]2

T

 and 
[image: image117.wmf]3

T


tandem compound, single reheatturbine time 
constants (
[image: image118.wmf]2

.

0

1

=

T

, 
[image: image119.wmf]6

2

=

T

 and 
[image: image120.wmf]4

.

0

3

=

T

 in seconds)

[image: image121.wmf]1

K

, 
[image: image122.wmf]2

K

 and 
[image: image123.wmf]3

K

tandem compound, single reheat cylinder 
fractions (
[image: image124.wmf]3

.

0

1

=

K

, 
[image: image125.wmf]4

.

0

2

=

K

 and 
[image: image126.wmf]3

.

0

3

=

K

)


[image: image127.wmf]i

D


system damping (
[image: image128.wmf]01

.

0

3

2

1

=

=

=

D

D

D

 in 
[image: image129.wmf]Hz

MW

pu

)
















_1275827720.unknown

_1289985916

_1290405828

_1290407486.unknown

_1290411795

_1290427662

_1290430087.unknown

_1290417557.unknown

_1290411484.unknown

_1290405855.unknown

_1290407233.unknown

_1290405838

_1289986582.unknown

_1290326743.unknown

_1290335502.unknown

_1290337448.unknown

_1290337583.unknown

_1290326746.unknown

_1290325178.unknown

_1290326737.unknown

_1290326740.unknown

_1290325181.unknown

_1290326734.unknown

_1289986614.unknown

_1290324621

_1289986597.unknown

_1289986366.unknown

_1289986395.unknown

_1289986450.unknown

_1289986414.unknown

_1289986379.unknown

_1289986300.unknown

_1289986351.unknown

_1289985997.unknown

_1289986214.unknown

_1275829075.unknown

_1275830333.unknown

_1275910476

_1289757967.unknown

_1289758747.unknown

_1276605037.unknown

_1277284503.unknown

_1275910297

_1275910332.unknown

_1275910350.unknown

_1275910324.unknown

_1275832755.unknown

_1275830352.unknown

_1275829484.unknown

_1275829547.unknown

_1275829742.unknown

_1275830318.unknown

_1275829560.unknown

_1275829527.unknown

_1275829292.unknown

_1275829451.unknown

_1275829181.unknown

_1275828598.unknown

_1275828919.unknown

_1275828925.unknown

_1275828935.unknown

_1275828613.unknown

_1275827740.unknown

_1275827801.unknown

_1275828584.unknown

_1275827808.unknown

_1275827792.unknown

_1275827731.unknown

_968663843

_1275824418.unknown

_1275827456.unknown

_1275827548.unknown

_1275827586.unknown

_1275827508.unknown

_1275827140.unknown

_1275827372.unknown

_1275824593.unknown

_1262766042.unknown

_1275824235.unknown

_1275824351.unknown

_1262766048.unknown

_968666551.unknown

_1262766040

_968664060.unknown

_968445075

_968540318

_968659017

_968661677

_968661164.unknown

_968579361.unknown

_968505305.unknown

_968538156

_968538456.unknown

_968505487

_968486959

_968445105

_968094900

_968094934

_968095032

_968182453

_968094960

_968094912

_967540431

_968094854

_968094866

_968094820

_960328211

_960328579

_960390978

_960328058

_960328205

